## Guidance&info
Questionnaire for Manufacturers
1. Introduction
Dear Madams and Sirs, The enquiry is is designed to gather data to determine the effect that Tier 2 efficiency requirements would have on weight and volume considering distribution transformers(MV/LV) that are designed for brown field projects, i.e. a replacement project that has specific limitations of size/weight restulting from the need to install the transformer in an existing enclosure. The primary objective of this enquiry it to gather sufficient information to assess if Tier 2 requirements of EU regulation 548/2014, applicable in 2021, are still technologically justified.The requirements were based on a previous enquiry for installers. More information on the scope of work can be found on the project website: https://transformers.vito.be/. This questionnaire document is intended to structure your data input to reflect the current and future situation in the transformer market (EU) appropriately. Each sheet consist of a base case designs based on typical brown field specifications (blue background cells). Please fill in where possible data for one or more Tier 1 and/or Tier 2 compatible designs that much as close as possible the type specifications (green background cells). The last columns of the 400&630 kVA also include 'greenfield' reference designs, i.e. cost effective designs for new projects where size and weight of the transformer is not a prespecified requirement resulting from limitations of existing enclosures. A separate sheet 'checkrange' is added to check the range of transformers with respect to Tier 2 in greenfield applications. NN means not nominated, please fill in when you don't want to disclose this data. Note that VTIO is committed to comply with antitrust rules. As a result, the present enquiry manufacturer data will be anomized. Therefore the market information and statistics collected will be treaded confidential by VITO and only non-identifiable, aggregated overall data will be published in the report of the review study. If an organization acts to collect this information on your behalf, such as T&D Europe, please ask them to treat and process this information accordingly. Manufacturers are requested to process this information request individually and results will not be published before sufficient information is collected to pubish non-identifiable data. The deadline to submit your answers is January 25th, 2017. Paul Van Tichelen on behalf of the project team Paul.vantichelen@vito.be Phone: +32 14 33 58 83 Sent to: transformers@vito.be
2. CONTACT DETAILS
· Organisation:
· Name:
· Position/Department:
· Telephone:
· E-mail:
Country of origin:

## 250kVA liq
|  | brownfied country specifications | [7 empty] | brownfield average | brownfield borderline | brownfield reference designs
country |  | BE | D | NL | F | PL | ES | N | N |  |  | type
sample (s) or representative ( r) |  | r | s REWAG2015 | r spec 11/2016 | r with protect. | s | r Iberdrola2014 | s | s Hafslund
Transformer category(1) |  | DT | DT | DT | DT-Enedis | DT | DT | DT | DT | DT | DT
Rated power of each winding (kVA) |  | 250/250/250 | 250 | 250 | 250 | 250 | 250 | 200 | 200 | 250 | 250
Number of phases |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Type (liquid / dry) |  | liquid | liquid | liquid | liquid | liquid | liquid | liquid | liquid | liquid | liquid
Rated voltage of each winding (kV) | high side (kV) | 15.4 | 20.8 | 23 | 20 | 21 | 20 | 22 | 22 | 20.8 | 23
| Low Side (kV) | 0.42 | 0.4 | 0.4 | 0.4 | 0.42 | 0.42 | 0.42 | 0.42 | 0.4 | 0.4
| Low Side (kV) 2 LV windings | brownfied country specifications BE: 0.242
Highest voltage for equipment of each winding Um (kV) | high side (kV) | 17.5 | 24 | 24 | 20 | 24 | 24 | 24 | 24 | 24 | 24
| low side (kV) | 3.6 | DIN EN 50386 | EN 50386 (1kV) |  | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 3.6
Vector Group(3) |  | DYN11a11 | DYN5 | DYN5 or DYN11 | DYN11 | DYN5 | DYN11 | Yyn0 or DYN11 | Yyn0 | Dyn11 | Dyn11
Regulation type |  | DETC |  | DETC |  | DETC | DETC | DETC | DETC | DETC | DETC
Tapping |  | brownfied country specifications NL: ±2x2.5%; brownfied country specifications ES: ±2x2.5% |  | ±2x2.5%
Type of cooling |  | onan | onan | onan | - | onan | onan | onan | onan | onan | onan
Impedance(6) [%] |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.45 | 4 | 4 |  | ? | ? | ? | ? | ?
max. length (mm) |  | 1200 | 1200 | 1200 | 1200 | 1350 | 1300 | 1200 | 1120 | 1221.25 | 1120 |  | ? | ? | ? | ? | ?
max. width (mm) |  | 700 | 800 | 800 | 800 | 900 | 910 | 750 | 750 | 801.25 | 700 |  | ? | ? | ? | ? | ?
max. heigth (mm) |  | 1245 | 1600 | 1600 | 1300 | 1700 | 1680 | 1500 | 1130 | 1469.375 | 1130 |  | ? | ? | ? | ? | ?
max. weight (kg) |  | 1200 | 1500 | 1360 | 1200 | 1200 | 1400 | NA | 1105 | 1280.7143 | 1105 |  | ? | ? | ? | ? | ?
Tier 1 (CkA0) or Tier 2(AkA0-10%) | [12 empty] | Tier 1 | Tier 2 | Tier 1 | Tier 2 | Tier 2
LV winding material | [12 empty] | Alu | Alu | Alu | Alu | Alu
HV winding material | [12 empty] | Alu | Alu | Alu | Alu | Alu
low loss steel (<0,9 W/kg@1,7T/50Hz) | [12 empty] | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg
oil type | [12 empty] | mineral | mineral | mineral | mineral | mineral
insulation type | [12 empty] | cellulose | cellulose | cellulose | cellulose | cellulose
operating temperature(Pk) | [12 empty] | 75°C | 75°C | 75°C | 75°C | 75°C
Estimated price increase in % of Tier 1 design
Sound power level |  | brownfied country specifications D: <47; brownfied country specifications NL: <47
Minimum clearance between live parts and ground [mm] |  | brownfied country specifications BE: EC60076-3; brownfied country specifications D: 55; brownfied country specifications NL: 100; brownfied country specifications N: IEC 60076-3
Minimum free distance required around the transformer [mm] |  | brownfied country specifications F: 150
Please clarify the reason for the constraints(8) and the consequence of exceeding them |  | existing substations | =+10 % allowed on dimensions | 100 mm clearance for fork lift note: AMDT are not allowed | Transformer is include in compact substation Max floor : 1200kg DSO need to manage faults on transformers and replace in existing substation ( weight, size..) | Size of door in existing substation, limits on pole weight

## 400 kVA liq
|  | brownfied country specifications | [5 empty] | brownfield average | brownfield borderline | brownfield reference designs | [5 empty] | Tier 1 greenfield reference design |  | Tier 2 greenfield reference design
country |  | BE | D | NL | PL | ES | N |  |  | type
sample (s) or representative ( r) |  | r | s REWAG2015 | r spec 11/2016 | s | r Iberdrola2014 | r
Transformer category(1) |  | DT | DT | DT | DT | DT | DT | DT | DT
Rated power of each winding (kVA) |  | 400/400/400 | 400 | 400 | 400 | 400 | 500 | 630 | 630
Number of phases |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Type (liquid / dry) |  | liquid | liquid | liquid | liquid | liquid | liquid | liquid | liquid
Rated voltage of each winding (kV) | high side (kV) | 15.4 | 20.8 | 23 | 21 | 20 | 22 | high side (kV) | 15.4
| Low Side (kV) | 0.42 | 0.4 | 0.4 | 0.42 | 0.42 | 0.42 | Low Side (kV) | 0.4
| Low Side (kV) 2 LV windings | 0.242
Highest voltage for equipment of each winding Um (kV) | high side (kV) | 17.5 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| low side (kV) | 3.6 | DIN EN 50386 | EN 50386 (1kV) | 1 | 1.1 | 1.1 | 1.1 | 3.6
Vector Group(3) |  | DYN11a11 | DYN5 | DYN5 or DYN11 | DYN5 | DYN11 | Yyn0 or DYN11 | Dyn11 | Dyn11
Regulation type |  | DETC |  | DETC | DETC | DETC | DETC | DETC | DETC
Tapping |  |  |  | ±2x2.5% |  | ±2x2.5% |  |  | ±2x2.5%
Type of cooling |  | onan | onan | onan | onan | onan | onan | onan | onan
Impedance(6) [%] |  | 4 | 4 | 4 | 4 and 4.5 | 4 | 4 | 4 | 4 |  | ? | ? | ? | ? | ? | ? | ? | ? | ?
max. length (mm) |  | 1250 | 1300 | 1320 | 1400 | 1620 | 1500 | 1398.3333 | 1250 |  | ? | ? | ? | ? | ? | ? | ? | ? | ?
max. width (mm) |  | 850 | 900 | 800 | 900 | 1020 | 900 | 895 | 800 |  | ? | ? | ? | ? | ? | ? | ? | ? | ?
max. heigth (mm) |  | 1300 | 1700 | 1600 | 1700 | 1750 | 2100 | 1691.6667 | 1300 |  | ? | ? | ? | ? | ? | ? | ? | ? | ?
max. weight (kg) |  | 1800 | 1800 | 1850 | 1500 | 1750 | NA | 1740 | 1500 |  | ? | ? | ? | ? | ? | ? | ? | ? | ?
Tier 1 (CkA0) or Tier 2(AkA0-10%) | [10 empty] | Tier 1 | Tier 2 | Tier 1 | Tier 2 | Tier 2
LV winding material | [10 empty] | Alu | Alu | Alu | Alu | Alu | Alu | Alu | Alu | Alu
HV winding material | [10 empty] | Alu | Alu | Alu | Alu | Alu | Alu | Alu | Alu | Alu
low loss steel (<0,9 W/kg@1,7T/50Hz) | [10 empty] | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg
oil type | [10 empty] | mineral | mineral | mineral | mineral | mineral | mineral | mineral | mineral | mineral
insulation type | [10 empty] | cellulose | cellulose | cellulose | cellulose | cellulose | cellulose | cellulose | cellulose | cellulose
operating temperature(Pk) | [10 empty] | 75°C | 75°C | 75°C | 75°C | 75°C
Estimated price increase in % of Tier 1 design
Sound power level |  |  | <50 | <50
Minimum clearance between live parts and ground [mm] |  | EC60076-3 | 55 | 100 |  |  | IEC 60076-3
Minimum free distance required around the transformer [mm]
Please clarify the reason for the constraints(8) and the consequence of exceeding them |  | existing substations | =+10 % allowed on dimensions | 100 mm clearance for fork lift note: AMDT are not allowed | Size of door in existing substation, limits on pole weight

## 630kVA liq
|  | brownfied country specifications | [7 empty] | brownfield average | brownfield borderline | brownfield reference designs | [5 empty] | Tier 1 greenfield reference design |  | Tier 2 greenfield reference design
country |  | BE | D | NL | F | PL | ES | N | S |  |  | type
sample (s) or representative ( r) |  | r | s REWAG2015 | r spec 11/2016 | r classical | s | r Iberdrola2014 | r | r
Transformer category(1) |  | DT | DT | DT | DT-Enedis | DT | DT | DT | DT | DT | DT
Rated power of each winding (kVA) |  | 630/630/630 | 630 | 630 | 630 | 630 | 630 | 630 | 800 | 630 | 630
Number of phases |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Type (liquid / dry) |  | liquid | liquid | liquid | liquid | liquid | liquid | liquid | liquid | liquid | liquid
Rated voltage of each winding (kV) | high side (kV) | 15.4 | 20.8 | 23 | 20 | 21 | 20 | 22 | 22 | 20.8 | 23
| Low Side (kV) | 0.42 | 0.4 | 0.4 | 0.4 | 0.42 | 0.42 | 0.42 | 0.42 | 0.4 | 0.4
| Low Side (kV) 2 LV windings | brownfied country specifications BE: 0.242
Highest voltage for equipment of each winding Um (kV) | high side (kV) | 17.5 | 24 | 24 | 20 | 24 | 24 | 24 | 24 | 24 | 24
| low side (kV) | 3.6 | DIN EN 50386 | EN 50386 (1kV) |  | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 3.6
Vector Group(3) |  | DYN11a11 | DYN5 | DYN5 or DYN11 | DYN11 | DYN5 | DYN11 | Yyn0 | Yyn0 or DYN11 | Dyn11 | Dyn11
Regulation type |  | DETC |  | DETC |  | DETC | DETC | DETC |  | DETC | DETC
Tapping |  | brownfied country specifications NL: ±2x2.5%; brownfied country specifications ES: ±2x2.5% |  | ±2x2.5%
Type of cooling |  | onan | onan | onan |  | onan | onan | onan | onan | onan | onan
Impedance(6) [%] |  | 4 | 4 | 4 | 4 | 4 and 4.5 | 4 | 4 or 6 | 5.8 | 4 | 4 |  | ? | ? | ? | ? | ? | ? | ? | ? | ?
max. length (mm) |  | 1500 | 1500 | 1500 | 1700 | 1400 | 1650 | 1550 | 1500 | 1537.5 | 1400 |  | ? | ? | ? | ? | ? | ? | ? | ? | ?
max. width (mm) |  | 850 | 900 | 820 | 920 | 900 | 1140 | 900 | 900 | 916.25 | 820 |  | ? | ? | ? | ? | ? | ? | ? | ? | ?
max. heigth (mm) |  | 1360 | 1800 | 1680 | 1650 | 1700 | 1870 | 2100 | 1400 | 1695 | 1360 |  | ? | ? | ? | ? | ? | ? | ? | ? | ?
max. weight (kg) |  | 2400 | 2500 | 2650 | 2500 | 2000 | 2400 | NA | 2300 | 2392.8571 | 2000 |  | ? | ? | ? | ? | ? | ? | ? | ? | ?
Tier 1 (CkA0) or Tier 2(AkA0-10%) | [12 empty] | Tier 1 | Tier 2 | Tier 2 | Tier 2 | Tier 1
LV winding material | [12 empty] | Alu | Alu | Alu | Alu | Alu | Alu | Alu | Alu | Alu
HV winding material | [12 empty] | Alu | Alu | Alu | Alu | Alu | Alu | Alu | Alu | Alu
low loss steel (<0,9 W/kg@1,7T/50Hz) | [12 empty] | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg
oil type | [12 empty] | mineral | mineral | mineral | mineral | mineral | mineral | mineral | mineral | mineral
insulation type | [12 empty] | cellulose | cellulose | cellulose | cellulose | cellulose | cellulose | cellulose | cellulose | cellulose
operating temperature(Pk) | [12 empty] | 75°C | 75°C | 75°C | 75°C | 75°C
Estimated price increase in % of Tier 1 design
Sound power level |  | brownfied country specifications D: <50; brownfied country specifications NL: <52 | <51 | <50
Minimum clearance between live parts and ground [mm] |  | brownfied country specifications BE: EC60076-3; brownfied country specifications D: 55; brownfied country specifications NL: 100; brownfied country specifications N: IEC 60076-3
Minimum free distance required around the transformer [mm] |  | brownfied country specifications F: 200
Please clarify the reason for the constraints(8) and the consequence of exceeding them |  | existing substations | =+10 % allowed on dimensions | 100 mm clearance for fork lift note: AMDT are not allowed | In urban areas, it would be impossible to address faults on transformers rated 630 to 1000 kVA in existing secondary substations, since the space would not be big enough and the pad would not be designed for higher weight. Max floor 2500 kg | Size of door in existing substation, limits on pole weight

## 100 kVA pole
|  | brownfied country specifications |  | brownfield reference designs
country |  | N | F | type
sample (s) or representative ( r) |  | r | r
Transformer category(1) |  | DT-pole | DT-pole &protect
Rated power of each winding (kVA) |  | 100 | 100
Number of phases |  | 3 | 3
Type (liquid / dry) |  | liquid | liquid
Rated voltage of each winding (kV) | high side (kV) | 22 | 20
| Low Side (kV) | 0.42 | 0.4
Low Side (kV) 2 LV windings
Highest voltage for equipment of each winding Um (kV) | high side (kV) | 24 | 20
| low side (kV) | 1.1
Vector Group(3) |  | Yyn0 | Dyn11
Regulation type |  | DETC
Tapping
Type of cooling |  | onan
Impedance(6) [%] |  | 4 | 4 |  | ? | ? | ? | ? | ?
max. length (mm) |  | 1100 | 1200 |  | ? | ? | ? | ? | ?
max. width (mm) |  | 700 | 1100 |  | ? | ? | ? | ? | ?
max. heigth (mm) |  | 1500 | 1300 |  | ? | ? | ? | ? | ?
max. weight (kg) |  | 750 | 550 |  | ? | ? | ? | ? | ?
Tier 1 (CkA0) or Tier 2(AkA0-10%) |  |  |  |  | Tier 1 | Tier 2 | Tier 2 | Tier 1 | Tier 1
LV winding material |  |  |  |  | Alu | Alu | Alu | Alu | Alu
HV winding material |  |  |  |  | Alu | Alu | Alu | Alu | Alu
low loss steel (<0,9 W/kg@1,7T/50Hz) |  |  |  |  | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg
oil type |  |  |  |  | mineral | mineral | mineral | mineral | mineral
insulation type |  |  |  |  | cellulose | cellulose | cellulose | cellulose | cellulose
operating temperature(Pk) |  |  |  |  | 75°C | 75°C | 75°C | 75°C | 75°C
Estimated price increase in % of Tier 1 design
Sound power level
Minimum clearance between live parts and ground [mm]
Minimum free distance required around the transformer [mm]
Please clarify the reason for the constraints(8) and the consequence of exceeding them |  | 100 kVA with weight 750 kg are sometimes mounted on single poles, but for new arrangements two poles are in most cases used for that weight. | ONLY ONE POLE Pole mounted is fixed by a support interface on a pole limited to 550 kg. Average aged of the pole 25/30 years. DSO need to manage faults on transformers in existing pole incident.

## 160 kVA pole
|  | brownfied country specifications | brownfield reference designs
country |  | F | type
sample (s) or representative ( r) |  | r
Transformer category(1) |  | DT-pole &protect
Rated power of each winding (kVA) |  | 100
Number of phases |  | 3
Type (liquid / dry) |  | liquid
Rated voltage of each winding (kV) | high side (kV) | 20
| Low Side (kV) | 0.4
Low Side (kV) 2 LV windings
Highest voltage for equipment of each winding Um (kV) | high side (kV) | 20
low side (kV)
Vector Group(3) |  | Dyn11
Regulation type
Tapping
Type of cooling
Impedance(6) [%] |  | 4 |  | ? | ? | ? | ? | ?
max. length (mm) |  | 1200 |  | ? | ? | ? | ? | ?
max. width (mm) |  | 1100 |  | ? | ? | ? | ? | ?
max. heigth (mm) |  | 1300 |  | ? | ? | ? | ? | ?
max. weight (kg) |  | 550 |  | ? | ? | ? | ? | ?
Tier 1 (CkA0) or Tier 2(AkA0-10%) |  |  |  | Tier 1 | Tier 2 | Tier 2 | Tier 1 | Tier 1
LV winding material |  |  |  | Alu | Alu | Alu | Alu | Alu
HV winding material |  |  |  | Alu | Alu | Alu | Alu | Alu
low loss steel (<0,9 W/kg@1,7T/50Hz) |  |  |  | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg | ≤0,9W/kg
oil type |  |  |  | mineral | mineral | mineral | mineral | mineral
insulation type |  |  |  | cellulose | cellulose | cellulose | cellulose | cellulose
operating temperature(Pk) |  |  |  | 75°C | 75°C | 75°C | 75°C | 75°C
Estimated price increase in % of Tier 1 design
Sound power level
Minimum clearance between live parts and ground [mm]
Minimum free distance required around the transformer [mm]
Please clarify the reason for the constraints(8) and the consequence of exceeding them |  | ONLY ONE POLE Pole mounted is fixed by a support interface on a pole limited to 550 kg. Average aged of the pole 25/30 years. DSO need to manage faults on transformers in existing pole incident.

## Checkrange
Tier 1/2 green field verification
Table 1 - Base and Boundary Case Descriptions
Case # | Base/Boundary | Application | Insulation Technology | Regulation Voltage Levels |  | Regulation Power Range (kVA) | Regulation 548/2014 Table Reference | Case Power Rating (kVA) | Case Voltage Rating |  | Tap changer | Tapping | Impedance | HV Insulation level | Sound power level
|  |  |  | high side (kV) | low side (kV) |  |  |  | high side (kV) | Low Side (kV)
| boundary lower | Distribution | liquid immmersed |  |  |  |  | 250 | 20…22 | 0.4 or 0.42 |  | ±5% | 4% | 125/49 | as per standard
1 | base | Distribution | liquid immmersed | <=24 | <=1.1 | <=3150 | 1.1 | 400 | 20…22 | 0.4 or 0.42 | DETC | ±5% | 4% | 125/50 | as per standard
1.1 | boundary upper | Distribution | liquid immmersed | <=24 | <=1.1 | <=3150 | 1.1 | 1000 | 20…22 | 0.4 or 0.42 | DETC | ±5% | 6% | 125/50 | as per standard
1.2 | boundary | Distribution /Industruial | liquid immmersed | <=24 | <=1.1 | <=3150 | 1.1 | 3150 | 20…22 | 0.4…0.69 | DETC | ±5% | 6% | 125/50 | as per standard
2 | base | industry transformer | dry type | <=24 | <=1.1 | <=3150 | 1.2 | 1250 | 20 | 0.42 ± 5% | DETC | ±2x2.5% | 6% | LI 125 / AC 50 | EN50588-1 Table 4
2.1 | boundary upper | industry transformer | dry type | <=24 | <=1.1 | <=3150 | 1.2 | 3150 | 20 | 0.42 ± 5% (or 0.69) | DETC | ±2x2.5% | 6% | LI 125 / AC 50 | EN50588-1 Table 4
2.2 | boundary lower | industry transformer | dry type | <=24 | <=1.1 | <=3150 | 1.2 | 400 | 20 | 0.42 ± 5% | DETC | ±2x2.5% | 6% (or 4%) | LI 125 / AC 50 | EN50588-1 Table 4
3 | base | pole mounted | liquid immersed | <=24 | <=1.1 | >25 & <315 | 1.6 | 100 | 20…22 | 0.4 or 0.42 | DETC | ±2.5% | 4% | 125/50 | as per standard
3.1 | boundary upper | pole mounted | liquid immersed | NA | <=1.1 | >25 & <315 | 1.6 | 315 | 20…22 | 0.4 or 0.42 | DETC | ±5% | 4% | 125/50 | as per standard
3.2 | boundary lower | pole mounted | liquid immersed | NA | <=1.1 | >25 & <315 | 1.6 | 25 | 25…33 | 0.4 or 0.42 | DETC | ±5% | 4% | 170/70 | as per standard
3.2 | sample | pole mounted/single phase | liquid immersed | NA | <=1.1 | >25 & <315 | 1.6 | 50 | 25…33 | 0.24…0.46 | DETC | ±5% | 4..4.5% | 170/70 | as per standard
4 | base | medium power | liquid immersed | 1.1 to 36 kV | NA | >3150 | 1.4 | 25000 | 33 | 11 | OLTC | ± 8x1.25% | 8% | LI 170 / AC 70 | Free
4.1 | boundary upper | medium power | liquid immersed | 1.1 to 36 kV | NA | >3150 | 1.4 | 31500 | 33 | 11 | OLTC | ± 8x1.25% | 10% | LI 170 / AC 70 | Free
4.2 | boundary lower | medium power | liquid immersed | 1.1 to 36 kV | NA | >3150 | 1.4 | 6300 | 33 | 11 | OLTC | ± 8x1.25% | 7% | LI 170 / AC 70 | Free
5 | base | medium power | dry type | 1.1 to 36 kV | NA | >3150 | 1.5 | 4000 | 30 | 0.69 | DETC | ±2x2.5% | 8% | LI 170 / AC 70 | Free
5.1 | boundary upper | medium power | dry type | 1.1 to 36 kV | NA | >3150 | 1.5 | 16000 | 30 | 11 (or 6.9) | DETC | ±2x2.5% | 8% or 10% | LI 170 / AC 70 | Free
6 | base | Large Power | liquid immersed | >36kV | NA | >3150 | 1.7 | 100000 | 132 | 33 | OLTC | ±8x1.25% | 0.125 | LI 650 / AC 275 | Free
7 | base | large Power | dry type | >36kV | NA | >3150 | 1.8 | 25000 | 66 | 20 | OLTC | ±8x1.25% | 10% | LI 325 / AC 140 | Free
All dry type design shall be:
# with AN
# Environmental condition 20/30/40 °C in accordance to EN 60076-11
# maximum temperature rise in accordance to the Insulation system, see EN60076-11
# reference temperature for losses in accordance to EN 50588-1 and EN 50629
4. ADDITIONAL QUESTION ON THE PRODUCT RANGE
| Apart from the boundary cases, are there any other types of transformers that might have difficultiest to meet the Tier 2 requirements that you are aware of? |  |  | No or Yes?
If yes, please specifiy

## datafields
Tier 1 | Cu | ≤0,9W/kg | mineral | cellulose | 75°C | yes
Tier 2 | Alu | >0,9W/kg | ester | polymer | >75°C | no
|  | NN | other | other